## Table 1
Location | Range | Detector type
Ex-core | power range: 1-100% thermal power | uncompensated ionization chambers with B10 -enriched boron lining
In-core | same as power range | fission chamber, U3O8

## Table 2
KKB Unit/Cycle | 1/49
Inlet Temperature [°F] | 534.56
Power [%] | 49.95
Flowrate [%] | 100
Cycle Average Burnup [GWd/t] | 2.15
Bank A/B/S Position | 320/258/320

## Table 3
Whole Bank (WB) Best Fit / Interval | 259 / 244-274
Close Group (CG) Best Fit / Interval | 260 / 244-274
Average RMS of Best Fit Trace | 2.44

## Table 4
FM name | RCCA position | WB Best Fit | CG Best Fit | Absolute Error WB | Absolute Error CG | Interval width WB | Interval width CG
FM1 | 297 | 301 | 301 | 4 | 4 | 24 | 24
FM2 | 281 | 282 | 283 | 1 | 2 | 29 | 29
FM3 | 310 | 309 | 310 | 1 | 0 | 20 | 20
FM4 | 297 | 302 | 302 | 5 | 5 | 23 | 23
FM5 | 295 | 299 | 299 | 4 | 4 | 26 | 26
FM6 | 300 | 302 | 302 | 2 | 2 | 23 | 23
FM7 | 299 | 295 | 297 | 4 | 2 | 28 | 28
FM8 | 292 | 288 | 290 | 4 | 2 | 37 | 37
FM9 | 294 | 299 | 299 | 5 | 5 | 24 | 24
FM10 | 310 | 310 | 310 | 0 | 0 | 16 | 16
FM11 | 282 | 282 | 284 | 2 | 2 | 27 | 27
FM12 | 290 | 295 | 295 | 5 | 5 | 26 | 26
FM13 | 289 | 289 | 290 | 0 | 1 | 31 | 31
FM14 | 294 | 297 | 298 | 3 | 4 | 25 | 25
FM15 | 292 | 294 | 295 | 2 | 3 | 30 | 30
FM16 | 310 | 310 | 310 | 0 | 0 | 16 | 16
FM17 | 290 | 293 | 293 | 3 | 3 | 30 | 30
FM18 | 310 | 309 | 310 | 1 | 0 | 19 | 19
FM19 | 287 | 290 | 290 | 3 | 3 | 31 | 31
Average Errors/Intervals |  |  |  | 3 | 3 | 26 | 26

## Table 5
FM name | RCCA position | WB Best Fit | CG Best Fit | Absolute Error WB | Absolute Error CG | Interval width WB | Interval width CG
FM20 | 280 | 281 | 282 | 1 | 2 | 36 | 36
FM21 | 239 | 239 | 239 | 0 | 0 | 41 | 41